BARKER SCOTT

CQC Compliance Templates

RISK ASSESSMENT

Fire Safety
Risk Assessment

For CQC-Registered Private Health Clinics

Private Health Clinic Sector

Document Reference: BS-PHC-RA-FS-002

Version 1.0

[Insert Organisation Name]

CONFIDENTIAL – FOR INTERNAL USE ONLY

# Document Control

| Document Title: | Fire Safety Risk Assessment |
| --- | --- |
| Document Reference: | BS-PHC-RA-FS-002 |
| Version: | 1.0 |
| Date of Issue: | [Insert Date] |
| Review Date: | [Insert Date + 12 Months] |
| Assessor: | [Insert Name / Role] |
| Approved By: | [Insert Name / Governance Lead] |
| Organisation: | [Insert Organisation Name] |
| Location / Site: | [Insert Clinic Address] |

# 1. Purpose

This risk assessment identifies fire hazards within [Insert Organisation Name], evaluates the risk to relevant persons, and establishes the fire safety measures required to comply with the Regulatory Reform (Fire Safety) Order 2005 (the FSO). It also supports compliance with Regulation 12 and Regulation 15 of the Health and Social Care Act 2008 (Regulated Activities) Regulations 2014.

# 2. Scope

This assessment covers all premises occupied by [Insert Organisation Name], including all clinical areas, reception, waiting areas, staff rooms, storage rooms, plant rooms, and external areas including car parks and bin stores. It applies to all employees, patients, visitors, and contractors.

# 3. Responsible Person

Under Article 3 of the FSO, the Responsible Person is [Insert Name / Clinic Director]. The Responsible Person holds overall accountability for fire safety and must ensure that this risk assessment is reviewed regularly, fire safety measures are maintained, and all relevant persons are informed.

# Risk Assessment Matrix

Risk is calculated as Likelihood × Severity using the 5×5 risk matrix below. Initial risk is assessed before additional controls; residual risk is the rating after implementation of all additional control measures.

| Likelihood ↓ / Severity → | 1 Negligible | 2 Minor | 3 Moderate | 4 Major | 5 Catastrophic |
| --- | --- | --- | --- | --- | --- |
| 5 – Almost Certain | 5 | 10 | 15 | 20 | 25 |
| 4 – Likely | 4 | 8 | 12 | 16 | 20 |
| 3 – Possible | 3 | 6 | 9 | 12 | 15 |
| 2 – Unlikely | 2 | 4 | 6 | 8 | 10 |
| 1 – Rare | 1 | 2 | 3 | 4 | 5 |

## Risk Rating Action Key

| Score | Rating | Required Action |
| --- | --- | --- |
| 15–25 | HIGH | Immediate action required. Escalate to Registered Manager and Clinical Lead. Consider suspending activity until controls are implemented. |
| 8–12 | MEDIUM | Action required within defined timescale. Implement additional controls and monitor. Report to governance meeting. |
| 4–6 | LOW | Manage by routine procedures and existing controls. Monitor for change. Review at scheduled intervals. |
| 1–3 | VERY LOW | No additional action required. Maintain current controls. Include in routine review cycle. |

# Hazard Identification and Risk Register

L = Likelihood (1–5) | S = Severity (1–5) | Risk = L × S. Existing controls are currently in place; additional controls are recommended actions to reduce residual risk.

| Ref | Hazard / Risk | Who is at Risk | Existing Control Measures | L | S | Risk | Additional Control Measures Required | L | S | Risk | Owner |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2.1 | Sources of ignition: electrical equipment, portable appliances, heating systems | All persons on premises | PAT testing annually Fixed electrical installation test (5-yearly) No unauthorised portable heaters policy | 2 | 5 | 10 | Electrical safety audit by competent person Thermal imaging survey of distribution boards Staff reminded re overloading sockets | 1 | 5 | 5 | Facilities Mgr |
| 2.2 | Sources of fuel: clinical waste, paper records, oxygen cylinders, alcohol-based products | All persons on premises | Housekeeping schedule maintained Oxygen stored per HTM 02-01 ABHR dispensers sited away from ignition sources | 2 | 4 | 8 | Quarterly fire safety walkthrough Reduce paper records through digitisation Review flammable storage arrangements annually | 1 | 4 | 4 | Fire Safety Lead |
| 2.3 | Inadequate means of escape: blocked exits, poor signage, locked doors | All persons on premises | Emergency lighting installed and tested monthly Fire exit signs illuminated Final exit doors openable without key from inside | 2 | 5 | 10 | Weekly fire exit check documented Annual emergency lighting certificate Escape routes included in induction tour | 1 | 5 | 5 | Fire Safety Lead |
| 2.4 | Failure of fire detection and alarm system | All persons on premises | Automatic fire detection system installed (BS 5839) Weekly alarm test from different call point Maintenance contract with competent provider | 2 | 5 | 10 | Six-monthly service by BAFE-registered engineer False alarm log reviewed quarterly System upgrade plan where obsolete components identified | 1 | 5 | 5 | Facilities Mgr |
| 2.5 | Patients with reduced mobility unable to self-evacuate | Patients with disabilities | Personal emergency evacuation plans (PEEPs) for known patients Evacuation chairs available at upper floors Staff trained in assisted evacuation | 2 | 5 | 10 | PEEP process included in patient registration Evacuation chair training refreshed six-monthly Drill includes simulated assisted evacuation annually | 1 | 5 | 5 | Reg. Manager |
| 2.6 | Staff unaware of fire procedures | Staff, Patients, Visitors | Fire safety training at induction Fire action notices displayed Evacuation drills six-monthly | 3 | 4 | 12 | Annual fire safety refresher training (all staff) Drill debrief with documented lessons learned Fire warden role assigned and identified by signage | 1 | 4 | 4 | Fire Safety Lead |
| 2.7 | Arson or deliberate fire-setting | All persons on premises | External bin stores secured and away from building CCTV operational Perimeter security maintained | 1 | 5 | 5 | Review arson risk as part of annual fire RA review Liaison with local fire and rescue service Letter box protection where applicable | 1 | 5 | 5 | Facilities Mgr |

# Applicable Legislation and Regulatory Framework

| Legislation / Regulation | Relevance |
| --- | --- |
| Regulatory Reform (Fire Safety) Order 2005 | Fire risk assessment, fire safety measures, and Responsible Person duties |
| Health and Social Care Act 2008 (Regulated Activities) Regulations 2014, Reg 12 & 15 | Safe premises and safe care |
| BS 5839 – Fire Detection and Alarm Systems | Design, installation, and maintenance of fire alarm systems |
| BS 9999 – Fire Safety in the Design, Management and Use of Buildings | Code of practice for fire safety |
| Health and Safety at Work etc. Act 1974 | General duty to ensure safety of employees and others |
| Management of Health and Safety at Work Regulations 1999 | Risk assessment and emergency procedures |
| HTM 02-01 – Medical Gas Pipeline Systems | Safe storage and use of medical oxygen |

# Risk Assessment Approval and Sign-Off

This risk assessment has been reviewed and approved by the following authorised personnel. By signing below, each confirms they have read, understood, and agree to implement the control measures identified.

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Registered Manager | [Insert Name] |  | [Insert Date] |
| Clinical Lead / Medical Director | [Insert Name] |  | [Insert Date] |
| Health & Safety Lead | [Insert Name] |  | [Insert Date] |
| CQC Nominated Individual | [Insert Name] |  | [Insert Date] |

# Version History

| Version | Date | Changes Made | Author | Approved By |
| --- | --- | --- | --- | --- |
| 1.0 | [Insert Date] | Initial issue | [Insert Name] | [Insert Name] |

Disclaimer: This risk assessment template is provided by Barker Scott Ltd as a general compliance resource for CQC-regulated private health clinics. It must be customised to reflect the specific hazards, operations, premises, and circumstances of [Insert Organisation Name]. Barker Scott Ltd accepts no liability for regulatory or health and safety outcomes arising from use of this template. Independent professional advice should be sought as appropriate.